Annex 1 to the Procurement Conditions

"Technical Specification"

technical specification

# STATIONARY GENERATOR

Public Body Central Project Management Agency is carrying out a public procurement procedure for the procurement of Stationary Generators for the Ministry of Finance of Ukraine (hereinafter referred to as the Beneficiary). The goods offered by the suppliers shall meet the requirements set out in this Technical Specification.

| No. | Feature | Technical specification requirement | Documents confirming compliance with the requirement |
| --- | --- | --- | --- |
|  | General requirements for the object of procurement |  |  |
| 1.1. | Object of procurement | Stationary diesel electric generator with delivery, installation and maintenance works. Generator should be manufactured, installed and configured in accordance with the requirements set out below. | The supplier declares compliance with this requirement in section 5 of the Tender form. Supplier must also provide manufacturer's technical documentation (catalogs, brochures) and/or product manufacturer's declarations (if the manufacturer's technical documentation does not fully reflect the compliance of the offered product with the requirements of the technical specification) or other equivalent documents proving the compliance of the offered product with the technical requirements |
| 1.2. | Quantity | 1 unit - Generator with a power of at least 650 kVA. | The supplier declares compliance with this requirement in section 5 of the Tender form. |
| 1.3. | Delivery location | 11 Mezhigirska str., Kyiv, | The supplier declares compliance with this requirement in section 5 of the Tender form. |
| 1.4. | Manufacturing the equipment | The equipment must be new and unused. Used or used and refurbished generators cannot be offered. | The supplier declares compliance with this requirement in section 5 of the Tender form. |
| 1.5. | Warranty | Generators must be covered by a warranty of at least 24 months or at least 1 000 engine hours, whichever comes first. The warranty of the generator must be provided by the Supplier and/or by the manufacturer and/or its representative in the service location indicated in the territory of beneficiary’s country, and if there are no service stations of the Supplier, manufacturer or its representative in the indicated territory, the equipment shall be transported and returned by the Supplier for warranty service at its own expense from the Beneficiary's places of deployment. | The supplier declares compliance with this requirement in section 5 of the Tender form and also submits the following supporting documents: |
| 1.6. | Documentation to be supplied with the generators | Generator must be supplied with printed maintenance and user manual in English and/or one of the official languages of the beneficiary. | The supplier declares compliance with this requirement in section 5 of the Tender form. |
| 2. | Technical requirements for generator and installation: |  |  |
| 2.1. | Functional characteristics of generators | Generators must have not less than these following functional characteristics: - Enclosed generators intended for outdoor installation, supplied with a weatherproof enclosure. - Intended as a backup power source for the building. - Rated output power (Standby rating): not less than 650 kVA. - Rated frequency: 50 Hz. - Rated voltage: 400/230 V. - Phase system: Three-phase. - Diesel engine suitable for the specified generator power and operating conditions. - Must have an integrated fuel tank ensuring operation for at least 5 hours under rated operating conditions. - Must provide automatic start upon loss of the main power supply and automatic shutdown when the main power supply is restored. - Must be equipped with a control and protection system providing monitoring, alarms and automatic shutdown in case of abnormal operating conditions. - Must be equipped with an integrated generator protection circuit breaker suitable for the rated output power. - Must be equipped with a manual emergency stop for immediate generator shutdown. - The generator set shall be CE marked and have its power ratings (Standby / Prime) defined in accordance with ISO 8528. | The supplier declares compliance with this requirement in section 5 of the Tender form. Supplier must also provide manufacturer's technical documentation (catalogs, brochures) and/or product manufacturer's declarations (if the manufacturer's technical documentation does not fully reflect the compliance of the offered product with the requirements of the technical specification) or other equivalent documents, confirming compliance with requirements in paragraphs No.1 through 7. |
| 2.2. | Installation | - The generators shall be installed as backup power sources for the building in compliance with all applicable safety, hygiene, construction and electrical regulations in force in the beneficiary country for this type of equipment. - The generators shall be installed on a designated base and at a safe distance from the building, in accordance with the manufacturer’s installation requirements. - The power cable connecting the generator to the building shall be suitable for the intended load and installed in compliance with all applicable electrical safety requirements. - The electrical power cable between the generator and the building shall be laid in accordance with safety requirements. The distance between the generator and the building connection point shall be between 10 and 30 meters. - The generators shall be fully assembled, tested and commissioned, including an automatic transfer switch (ATS) ensuring automatic transfer of load to the generator upon loss of the main power supply and automatic retransfer upon restoration of the main power supply. | The supplier declares compliance with this requirement in section 5 of the Tender form. |
| 2.3 | Maintenance | The supplier shall ensure regular preventive maintenance of the generator during the warranty period, performed in accordance with the manufacturer’s recommendations, at least once per year. | The supplier declares compliance with this requirement in section 5 of the Tender form. |

NOTES:

Where the technical specification indicates a specific model or source of supply, a specific process specific to the goods or services supplied by a particular supplier, or a trademark, patent, types, specific origin or manufacture, it shall be understood that these characteristics are indicative only and that the suppliers are free to offer an equivalent option. The supplier must demonstrate the equivalence referred to in this paragraph.

In the event that the technical specification specifies values/parameters for a particular technical characteristic, suppliers may offer goods whose values/parameters are not inferior to those specified (goods with no inferior characteristics may be offered).